## Sheet1
PID tuning charts by POES-Weather Ltd March 14th 2012
Version 2

		Input
		Ultimate gain KU:	1
		Oscillation period TU:	1

The Ziegler–Nichols tuning method is a heuristic method of tuning a PID controller.
It was developed by John G. Ziegler and Nathaniel B. Nichols.
It is performed by setting the I (integral) and D (derivative) gains to zero. The "P" (proportional) gain,
KP is then increased (from zero) until it reaches the ultimate gain KU, at which the output of the control
loop oscillates with a constant amplitude.
KU and the oscillation period TU are used to set the P, I, and D gains depending on the type of controller used.

		Ziegler–Nichols Tuning Chart
		Control type	KP	KI	KD
		Classic PID	0.5882	0.5000	0.1250
		Pressen Integral Rule	0.7000	0.4000	0.1500
		Some overshoot	0.3333	0.5000	0.3333
		No overshoot	0.2000	0.5000	0.3333

Ziegler-Nichols tuning creates a "quarter wave decay".
This is an acceptable result for some purposes, but not optimal for all applications.
The Ziegler-Nichols tuning rule is meant to give PID loops best disturbance rejection performance.
This setting typically does not give very good command tracking performance.

Ziegler-Nichols yields an aggressive gain and overshoot:
Some applications wish to instead minimize or eliminate overshoot, and for these Z–N is inappropriate.

As an alternative to the table above, another set of tuning values have been determined by Tyreus and Luyblen
for PI and PID, often called the TLC tuning rules.
These values tend to reduce oscillatory effects and improves robustness.

		Tyreus-Luyben Tuning Chart
		Control type	KP	KI	KD
		PID	0.4545	2.2000	0.1587

Sources:	http://en.wikipedia.org/wiki/Ziegler–Nichols_method
	http://www.chem.mtu.edu/~tbco/cm416/zn.html
	https://controls.engin.umich.edu/wiki/index.php/PIDTuningClassical#Ziegler-Nichols_Method
	http://www.mstarlabs.com/control/znrule.html